## Slide 1: CFD Simulation of the Target Door for Water Temperature Limits
Geunhyeong Lee
5/5/2025

## Slide 2: Overview
Target door CFD simulation was perform to know the water temperature limitation (< 100 )
  Thermal load: 1~6 kW deposited power on the front door
  Limitation: heat surface was assumed same heat distribution
Current heat exchanger performance was estimated by the COMSOL results
Remarks
  Current heat exchanger would sustain by ~50 kW of primary beam power at 25% heat deposition
  The detailed performance estimation should be coupled with target system heat deposition

## Slide 3: Simulation condition
Geometrical model
  Unnecessary holes were removed
Fluid in
Fluid out

## Slide 4: Simulation condition
Mesh
  Using the default mesh in ANSYS Fluent
  5 inflation layers were added to improve turbulent flow resolution
  Min. Orthogonal Quality: 0.15
  Max. Aspect Ratio: 18
Overall mesh shape
Fluid path mesh

## Slide 5: Simulation condition
CFD simulation condition
  Model:
    Turbulent flow, Realizable k-e, Standard wall function (Reynolds number ~ 6840)
      Model constant as default
  Material:
    Fluid: Water (from ANSYS)
    Solid: Copper (from ANSYS, Cp: 381 , k: 387.6 )
  Boundary condition
    Inlet: velocity (0.48 m/s, calculated by 0.375 GPM)
    Outlet: pressure (0 Pa)
    Surface heat flux: 1~6 kW
Reference data

## Slide 6: Simulation condition
Convergence condition: 1e-6 for all residuals, converged in ~440 iterations.

## Slide 7: Simulation results
Temperature results at 4 kW

## Slide 8: Target System Simulation Results (COMSOL)
Front door radiative heat flux calculated by COMSOL ( = 0.85 at all surface)
  28.1 % heat deposited at the front door
    for reference, 16.9 % heat deposited at the back door)
Radiative heat flux distribution on the front door at 30 kW heat deposition

## Slide 9: Conclusions
The CFD simulation for the target system front door was performed
  The CFD results assumed uniform heat deposition on the door surface
  The outer surface area receives more heat; this should be considered for accurate estimation
If the target deposition is 25% under the full coating condition, it could support a primary beam power of 52 kW before reaching a water temperature of 100
T [] = 16.9Q [kW] + 38
3.67 kW